## Slide 1: Fault Detection for the Control of Supermarket Refrigeration Systems
Zoltan Mark Pinter
Supervisors: Hans Henrik Niemann, Dimitrios Papageorgiou
External Supervisor: Lars Finn Sloth Larsen
3th September, 2019

## Slide 2: Introduction
The gas loop
  Measurement error
  Effects: reducing efficiency and heating cabinets
Project goal
  Early detection and fault accommodation
  Gas loop shall not be entered
Project scope
  Field experiment and simulation
    Residual generation
    Fault detection
    Measurement reconstruction
  Simulation
    Fault accommodation
  Operation domain: 10...30 °C

## Slide 3: Schedule
Gas Loop Problem
Physical and Mathematical Model
  Simplifications
Short introduction to the investigated plants
State estimator
  Residual analysis
Recursive Least Squares (RLS) algorithm
Fault Detectors
Results and Evaluation
Conclusion and Discussion

## Slide 4: The gas loop

## Slide 5: Physical model
Back-end and front-end
  Different dynamics

## Slide 6: Mathematical model – differential equations
Goal: state space model description
Applied differential equations
  Mass balance equation
  Energy balance equation
  Chain rule
    Two properties: given by the phase rule
  Low pass filter

## Slide 7: Mathematical model – heat transfer
Discretization of gas cooler: equal volume cells
Energy balance
Most assumptions are made here
  Linear resistance model
  First order convection model
  Unknown time constant
  Neglected spatial temperature difference distribution

## Slide 8: Mathematical model - simplifications
Main problems
  Controllability issues
  Information distribution of estimator
  Large range of partial differentials
Solutions
  No bypass valve and heat recovery unit
  One-cell gas cooler
  Perception of dynamics
  Look-up table, assuming steady state

## Slide 9: Mathematical model
Nonlinear model
Disturbance: enthalpy difference
Linearization
  Analysis at a set-point
Conversion to discrete time (1s)

## Slide 10: The plants
Field experiment
Simulation

## Slide 11: The state estimator

## Slide 12: Parameter estimation and residuals
The main challenges are
  Set-point change has the same effect as the fault
  Dynamical signals
  Non-Gaussian noise
Physical background
  Energy accumulation should be bounded in the gas cooler

## Slide 13: Parameter estimation and residuals
Recursive linear Least Squares (RLS)
Regularization and robustness
  The ambient temperature perturbed the system sufficiently
  Forgetting factor
Time delays
Problem with information density
Residual whitening: less normal signals

## Slide 14: Fault Detection
Signal choices
  Residual for detection: heat transfer
  Residual for reconstruction: enthalpy
Log likelihood ratio
CUSUM
GLR
  Window length: 100 s

## Slide 15: Fault Detection – Expectation Maximization
Latent variable models
E step: changing the structure
M step: changing the parameters

## Slide 16: Fault Detection – Expectation Maximization
Gaussian Mixture Model (GMM) with two clusters:
  Normal and faulty operation clusters
The following log likelihood is maximized:
Window length: 10 s

## Slide 17: Fault handling
Fault handling does not stop until human intervention
Strong detectibility and measurement reconstruction are achieved by freezing the parameter values after detection

## Slide 18: Results and Evaluation
Objectives
  Fault detectors
  Measurement reconstruction
Application
  Control performance
  State estimation quality

## Slide 19: Results and Evaluation - fault diagnosis
Residual signals: strong detectibility
Fault detector
  Detection times

## Slide 20: Results and Evaluation - fault diagnosis
Fault detector
  Area under the ROC curve, and sensitivity index

## Slide 21: Results – measurement reconstruction
For simulations, insulation fault scenario is considered

## Slide 22: Results and Evaluation – control performance
Coefficient of performance
Cabinet temperatures
Inputs are no longer saturated

## Slide 23: Results – state estimation quality
Only simulations considered – values can be extracted for analytical approximations
CPU running time depends on set-point sampling rate

## Slide 24: Results – state estimation quality

## Slide 25: Conclusion
Robust residual signals are generated
  Can be used for early detection and measurement reconstruction
  Works for field experiment data as well
  Application evaluation
Challenges
  Fault diagnosis is harder, where the effects are less pronounced
  Change of operation-point has the same effect on state estimator residuals, as the faults
Findings
  Estimator capturing the most important traits of the system
  RLS with physical assumption as residual generator of a nonlinear system
  Expectation Maximization online fault tracking algorithm

## Slide 26: Future work
Field experiments with fault handling
Extending operation domain to include bypass valve and heat recovery unit as well
Evaluating the EM detector in a more equal environment and testing fault isolation
Using estimator for prediction and enhancing advanced control strategies

## Slide 27: Thank you for the attention!

## Slide 28: Appendix

## Slide 29: Refrigeration systems

## Slide 30: Residual whitening
Applying the inverse filter of
Input signal: ambient temperature
Main criteria
Results

## Slide 31: Fault Detection – Expectation Maximization
Gaussian Mixture Model (GMM) with two clusters:
  Normal and faulty operation clusters
The following log likelihood is maximized:
Window length: 10 s

## Slide 32: Results – measurement reconstruction
For simulations, insulation fault scenario is considered

## Slide 33: Results – state estimation quality
Only simulations considered – true values can be extracted
  Weighted average is considered for virtual enthalpy of gas cooler:
CPU running time depends on set-point sampling rate

## Slide 34: Corrections
The line widths in the following figures are not everywhere correct:
The E and M steps are not well noted in this figure: