## Slide 1: Fault detection of a supermarket refrigeration system
Zoltan Mark Pinter
Supervisors: Hans Henrik Niemann, Dimitrios Papageorgiou
External Supervisor: Lars Finn Sloth Larsen

## Slide 2: Refrigeration systems – our source of happiness

## Slide 3: Refrigeration system

## Slide 4: Notations
Cheat sheet
  Take enthalpy as energy
  If pressure increases, temperature increases
  If pressure increases, density increases
  If enthalpy increases, density decreases
  If enthalpy increases, temperature, or vapour ratio of 2 phases (def.: quality) increases
  Above saturation curve: 1 phase, below: 2 phases
  Left side of saturation curve: liquid

## Slide 5: Refrigeration system, project scope
Range: 10…30 degrees

## Slide 6: Project Goal: Gas Loop Detection, and fault tolerant control
Temperature measurement has negative offset
  Fans stop, enthalpy, then pressure increase, until compressors are saturated
Gas in cycled quickly in system without achieving necessary heat transfer
Efficiency drops and cabinets heat up
Goals:
  create residuals for detection, then detect
  Create necessary

## Slide 7: Differential equations
Partial differentials
Mass balance
Energy balance
Low pass filter
Main assumption: equilibrium

## Slide 8: Model Description
Volume equations (for cells): density, enthalpy, pressure changing
Concentrated component equations: mass flow rate changing
Spatial temperature difference distribution
Flow resistance
Valve equation
Compressor equation: current generator
Air temperature state
Disturbance

## Slide 9: Model Description
Spatial temperature difference distribution
Air temperature state
Disturbance

## Slide 10: Simlifications
Problems
  Negligible details: fast dynamics, pressure change contribution to enthalpy change
  Parameter uncertainty: unknown time constants
  Controllability issues: derivatives
  Observability issues: gas cooler
  Too many states for estimator
  Partial differentials cover several order of magnitudes

## Slide 11: Simlifications
Solutions
  Not derivatives, but states were connected
  Density and enthalpy are ‘true states’, pressure and temperature are ‘projected states’, connected with fast dynamics
  Only one cell in gas cooler
  Constraint as measurement
  No actuator dynamics

## Slide 12: Simlifications

## Slide 13: Residual Generation
LTV estimator -> parameters are dependent on states -> high Kalman gain is needed to avoid getting stuck in local minima
  Residuals provide very weak detectibility
New strategy: based on only measurements and physical assumptions
  Steady state energy balance, small deviations during transients
  Large deviations: something ‘special’ entered the system
  Fault detection: freezing parameter values until fault disappears

## Slide 14: Recursive Least Squares
No dynamics assumed

## Slide 15: Expectation Maximization Fault Detector
Minimizing log-likelihood of two Gaussian Mixture Model clusters:
  Faulty, non faulty
Intuitive idea: a cluster with large variance gives higher density on faulty residual values

## Slide 16: Expectation Maximization Fault Detector
Intuitive idea: a cluster with large variance gives higher density on faulty residual values

## Slide 17: Residual Whitening, structure criteria

## Slide 18: Residual Whitening, results
Non-normality became stronger
Whiteness enforced

## Slide 19: Fault Detection, simulation

## Slide 20: Fault Detection, field data

## Slide 21: Fault Operation, simulation

## Slide 22: Fault Operation, field data

## Slide 23: Conclusion
Residual is created, fault detection is done
  CUSUM needs further investigation
Further topics of the thesis
  Linear analysis of a set-point (system dynamics check)
  LTV Kalman filter (with or without constraints)
  Fault detection based control (distributed PI controller) comparison
    Do the results improve?

## Slide 24: Thank you for the attention!