## Slide 1: Fault Detection for the Control of Supermarket Refrigeration Systems
Zoltan Mark Pinter
Supervisors: Hans Henrik Niemann, Dimitrios Papageorgiou
External Supervisor: Lars Finn Sloth Larsen
3th September, 2019

## Slide 2: Schedule
Introduction
  Gas Loop Problem
  Project goal
  Project scope
Physical and Mathematical Model
Short introduction to the investigated plants
State estimator
  Residual analysis
Recursive Least Squares (RLS) algorithm
Fault Detectors
Results and Evaluation
Conclusion and Discussion
Notes: Gas loop: measurement error, reducing efficiency, heating up cabinets
Project goal: early detection and fault accommodation
Project scope: field experiment and simulation
Operation domain: 10…30 degrees.
Fault diagnosis problem is separated.
Rest of schedule

## Slide 3: Physical model
Back-end and front-end
  Different dynamics
Notes: Front end: distributed control for all cabinets, swift dynamics, boundary condition
Main components (left)
Gas cooler is divided to equal control volume cells, as heat transfer depends on spatial distribution of properties
2 cell for initial, 1 cell for final model
Where the fault occurs.
Parts of ph diagram
Mass flow rates

## Slide 4: The gas loop
Notes: Controller perceives the left figure version
Enthalpy temperature gradient magnifies the effect.
Higher enthalpy passed to receiver. Increasing pressure, saturating IT compressor
Cabinets heat up

## Slide 5: Mathematical model – differential equations
Goal: state space model description
Applied differential equations
  Mass balance equation
  Energy balance equation
  Chain rule
    Two properties: given by the phase rule
  Low pass filter

## Slide 6: Mathematical model – heat transfer
Energy balance
Most assumptions are made here
  Linear resistance model
  First order convection model
  Neglected spatial temperature difference distribution
for cells

## Slide 7: Mathematical model - simplifications
Main problems
  Controllability issues
  Information distribution of estimator
  Large range of partial differentials
Solutions
  No bypass valve and heat recovery unit
  One-cell gas cooler
  Perception of dynamics
  Look-up table, assuming steady state

## Slide 8: Mathematical model
Nonlinear model
Disturbance: enthalpy difference
Linearization
  Analysis at a set-point
Conversion to discrete time (1s)
Notes: List the final states on the figure!

## Slide 9: The plants
Field experiment
Simulation
Notes: The two plants
Step fault: switch-on switch-off
For the Modelica plant, insulation
Ambient temperature: increasing amplitude for testing estimator robustness

## Slide 10: The state estimator
Fault handling (optional)
Inner fold: linear dynamical
Kalman filter
Set point selection
Outer fold: steady state filter
Notes: Two different sampling times
Fault handling is independent from state estimator for modularity
Describe parts
Innovation: operation point change same effect as fault

## Slide 11: Parameter estimation and residuals
The main challenges are
  Set-point change has the same effect as the fault
  Dynamical signals
  Non-Gaussian noise
Physical background
  Energy accumulation should be bounded in the gas cooler
Notes: Main challenges
Physical background: heat flow rate should be the linear combination of the energy flow rates
Error of this assumptions is caused by transients, energy accumulation
Error is bounded in case of normal operation

## Slide 12: Parameter estimation and residuals
Recursive linear Least Squares (RLS)
Problem with information density
Regularization and robustness
  The ambient temperature perturbed the system sufficiently
  Forgetting factor
Time delays
Residual whitening: less normal signals

## Slide 13: Fault Detection
Signal choices
  Residual for detection: heat transfer
  Residual for reconstruction: enthalpy
Log likelihood ratio
CUSUM
GLR
  Window length (M) : 100 s
2

## Slide 14: Fault Detection – Expectation Maximization
Latent variable models
E (expectation) step: changing the structure
M (maximization) step: changing the parameters
Notes: Algorithm from field machine learning, to maximize likelihood for latent variable models
Latent variable model: there are unobserved variables, which are projected on the data.
E step. Changing the structure is to minimize the misfit between the distributions, which is called the KL divergence
M step: parameters are modified to maximize likelihood

## Slide 15: Fault Detection – Expectation Maximization
Gaussian Mixture Model (GMM) with two clusters:
  Normal and faulty operation clusters
The following log likelihood is maximized:
Window length: 10 s
Notes: GMM with two clusters
Window length of 10 data
Prob. density value for normal operation cluster is higher, its responsibility is higher
The more the mean diverges, the swifter the fault tracking becomes, as the faulty cluster takes more responsibility
When the prob. density value of the faulty cluster is higher, alarm is fired.

## Slide 16: Fault handling
Fault handling does not stop until human intervention
Strong detectibility and measurement reconstruction are achieved by freezing the parameter values after detection

## Slide 17: Results and Evaluation
Objectives
  Fault detectors
  Measurement reconstruction
Application
  Control performance
  State estimation quality

## Slide 18: Results and Evaluation - fault diagnosis
Residual signals: strong detectibility
Fault detector
  Detection times
Notes: Strong detectbility is guaranteed.
Left side, right side
CUSUM: slowness. GLR: false alarms. EM: missed detection
Threshold dependency

## Slide 19: Results and Evaluation - fault diagnosis
Fault detector
  Area under the ROC curve, and sensitivity index
Notes: Threshold free method: AUC, directly relates to the better scaled sensitivity index from the field of signal processing
Best classifier: enthalpy residual, but slow dynamics: large detection time
Best detectors for this case: GLR and EM

## Slide 20: Results – measurement reconstruction
For simulations, insulation fault scenario is considered
Notes: Insulation fault scenario is considered
Left box: up: no fault handling, down: fault handling
Since new operation points are discovered outside of normal operation, large estimation errors
Right box: temperature fault estimation. Due to small perturbance of regressors, 30% of error

## Slide 21: Results and Evaluation – control performance
Coefficient of performance
Cabinet temperatures
Inputs are no longer saturated
Notes: COP ratio
Left box: COP and evaporator outlet h (relate to cabinet temperatures), right box: inputs for simulation and field experiment
Two fault scenario results are identical, no effect of fault
COP decreases if no fault handling
Evaporators, after latent period control objectives are not achieved due to saturations
Saturation is inspected for both

## Slide 22: Results – state estimation quality
Notes: Only simulations considered – values can be extracted for analytical approximations
Left box: states are well estimated for both
Temperature: large accuracy (not handled), low precision (handled)
Due to the assumptions of heat transfer model
Prediction: overestimation of convection

## Slide 23: Conclusion
Robust residual signals
  Early detection and measurement reconstruction
  Gas loop is not entered
Challenges
  Fault diagnosis is harder, where the effects are less pronounced
  Change of operation-point has the same effect on state estimator residuals, as the faults
  Information density was low for field experiment data
Findings
  Estimator
  Residual generator for the nonlinear system
  Expectation Maximization algorithm
Notes: Robust residuals: early detection and measurement reconstruction, no gas loop
Works for field experiment data as well, tested for applications
Challenges (from slide)
Findings: estimator capturing the most important traits of the system
RLS with physical assumption
Expectation Maximization online fault tracking algorithm

## Slide 24: Future work
Field experiments with fault handling
Extending operation domain to winter conditions
Evaluating the EM detector in a more equal environment and testing fault isolation
Using estimator for prediction and enhancing advanced control strategies

## Slide 25: Thank you for the attention!

## Slide 26: Appendix

## Slide 27: Refrigeration systems

## Slide 28: Residual whitening
Applying the inverse filter of
Input signal: ambient temperature
Main criteria
Results

## Slide 29: Fault Detection – Expectation Maximization
Gaussian Mixture Model (GMM) with two clusters:
  Normal and faulty operation clusters
The following log likelihood is maximized:
Window length: 10 s

## Slide 30: Results and Evaluation - fault diagnosis
Residual signals: strong detectibility
Fault detector
  Detection times
Notes: Strong detectbility is guaranteed.
Left side, right side
CUSUM: slowness. GLR: false alarms. EM: missed detection
Threshold dependency

## Slide 31: Results – measurement reconstruction
For simulations, insulation fault scenario is considered

## Slide 32: Results – state estimation quality
Only simulations considered – true values can be extracted
  Weighted average is considered for virtual enthalpy of gas cooler:
CPU running time depends on set-point sampling rate

## Slide 33: Corrections
The line widths in the following figures may be misleading:
The following equation is not squared:
The E and M steps are not well noted in this figure:
2