## Sheet1
| Found |  |  | Description
Sensor and measurement, fault detection
Virtual temperature sensor | 1 | https://findit.dtu.dk/en/catalog/239836161 |  | Steady state thermodynamical and empirical equations are used with linear regression, to find the mass flow rate in a single level HVAC system. 6 sensors are used for heating and 4 for cooling. Wild range of operating conditions.
Mass flow rate estimation | 1 | https://findit.dtu.dk/en/catalog/2289206109 |  | HVAC. Empirical and further ANSI/ARI 540-1999 equations are used to find mass flow rates. Linear regression is used. Different equations were needed for different components, eg for fixed and variable speed compressors. For the TXV valve, analytic equations are used. Bayesian log likelihood estimation was used to find if there is fault. The refrigerant flow faults are correctly decoupled from other faults.
Sensor configuration | 1 | https://findit.dtu.dk/en/catalog/2386877834 |  | Linear analytic equations were used to find the location of sensors in the refrigerant cycle. A test signal at a given frequency was used (active identification, in a range which is not too corrupted by disturbances and noise) to configure. Assuming that the frequency signal acts with different magnitudes on the measurements of different signals, GLRT was used to identify sensors. A weight matrix was used on the residuals to reduce the effect of the residuals at the test frequency. Lab experiments showed worse results than simulation ones.
KF based fault isolation | 1 | https://findit.dtu.dk/en/catalog/2389359423 | https://findit.dtu.dk/en/catalog/230618367 | Chiller. Lars's half empirical half analytic model is used for modelling. Model is discretized and the residual is normalized by variance. CUSUM is applied. Two isolation method are determined. One sensor per filter is better for isolating multiple fault scenarios, while filter applied for all but one sensor is more robust to plant deviations (Isermann, 2006). Multiple Model Adaptive Estimation (this is likelihood maximization based) is used. Extended version worked better than linear.
Fault diagnosis with ANN and fuzzy | 1 | https://findit.dtu.dk/en/catalog/273389845 |  | Linguistic rules determined a rule base, upon which an ANN was built. 7 different faults were detected and isolated. The method gives linguistic decisive functions. Sensor malfunctions were identified as well. False positive rates were not checked.
IO based fault isolation | 1 | https://findit.dtu.dk/en/catalog/2389359418 |  | Chiller. UIO is used, conditions are stated then Lars's model is applied. Wide variety of conditions were tested, UIO did not work well during the nights. UIO was undercompeting against KF for sensor fault isolation, but overcompeting in parametric fault isolation. Detections were similarly effective.
PCA based sensor fault detection | 0 | https://findit.dtu.dk/en/catalog/2372744920
Sensitivity of PCA based sensor fault detection | 1 | https://findit.dtu.dk/en/catalog/2289746875 |  | In this project every sensor got their own Q test threshold. 8 sensor measurement and the chiller energy balance equations were used. SCREE test is used to find the optimal number of principal components. It is empirically shown that the condenser temperatures have bigger range than the evaporator ones. Outlier are removed again.
Low charge detection with Eureqa | 1 | https://findit.dtu.dk/en/catalog/2391171426 |  | Non-ciritically charged refrigeration systems are fault diagnosed by the Eureqa sofware. The symbolic regression is an evolutionary computation method based that looks into space for a mathematical expression. while minimizing different error metrics. Low and middle temperature level data are trained independently.
Detecting fault with energy signals | 1 | https://findit.dtu.dk/en/catalog/2292556230 |  | HVAC. Energy consumption of actuators in the fron-end were investigated. SARIMA model is identified: composing of ARMA and seasonal ARMA. Defrost cycles needed to be ignored. Segmented linear trends were assumed for modelling (to overcome nonlinearity). Single treshold is used, and for evaluation Gscor=sqrt(precision x recall). Without using sensors, the results were note convincing, but including them increased performance.
Decision tree based fault diagnosis | 1 | https://findit.dtu.dk/en/catalog/2391697971 |  | HVAC. The same sensors are used as in the virtual sensor articles (half analytic half experimental models). Support vector regression is used to fit nonlinearities more. CART algorithm creates the trees Pruning is applied against overfitting, and expert knowledge rules are also used for pruning. Confusion matrix, accuracy are used for evaluation. Tests on varying operating conditions but different training conditions give 69.18% accuracy.
SVDD based chiller fault detection | 1 | https://findit.dtu.dk/en/catalog/2358353002 | https://findit.dtu.dk/en/catalog/245596364 | It is shown, that the variables in refrigeration systems are rather non Gaussian, with Shapiro-Wilk test. Eight or 16 variables are used to compare to PCA-PC subspace methods. It outperforms it, pbecause PCA assumes Gaussian distribution, linear process variables, and is not adapting to several operating conditions.
PCA-R-SVDD based chiller fault detection | 1 | https://findit.dtu.dk/en/catalog/2290056945 |  | The following methods are compared: PCA, SVDD, PCA-PC-SVDD and PCA-R-SVDD. For PCA, here not only the Q, but T (transformation or so called score matrix) boundaries are introduced. For PCA-X-SVDD, SVDD is applied on the subspaces, then the analytic equations of the two methods are merged. There are hyperparameters for SVDD, which need to be tuned with 10-fold cross validation. Kernel is Gaussian. The confidence level of fault detection is emprically assigned to 95%. The disadvantages of SVDD are described: cannot take uncertainty into consideration, higher FAR for training on data with limited operating conditions, high computational complexity. Steady state detection of Rossi with forgetting factor is used. For less severe fault levels, PCA-R-SVDD outperforms its competitors.
PCA-R-BN fault detection for chillers | 1 | https://findit.dtu.dk/en/catalog/2435491725 |  | Since BN does not have good detection accuracies for low fault levels, PCA-R-BN architecture was tested. It is compared to PCA, PCA-PC, and BN. Two levels are used to define probability layers, fault and sympton levels, then the principle of the maximum posterior probability was used. Maximum likelihood is used to find the conditional probability parameters, and expert knowledge is used to find prior probability parameters. The distance rejection model of Verron et al. was used to detect faults. Nine variables are selected for detection. The methods were tested on a physical plant.
Adaptive PCA for chiller fault detection | 1 | https://findit.dtu.dk/en/catalog/232266016 |  | HVAC. Data based technique: Q boundary rule is used to find new trends in the PC subspace. It was trained in normal operation by removing rows not fitting the normal assumption. This resulted in a less conservative threshold. False positives were not evaluated. Steady state detection is used.
Identification of too high evaporator temperatures with ML | 1 | https://findit.dtu.dk/en/catalog/2441680591 |  | Logistic Regression, decision trees and random forest (ensemble model of decision tree with bagging and subspace sampling) are tested on industrial refrigeration system. The last one outperfromed the others in F1-score.
Identification, optimization (no control)
Nonlinear system identification | 0 | https://findit.dtu.dk/en/catalog/2347764419
Fuzzy modelling and identification, intelligent control for compressor | 0 | https://findit.dtu.dk/en/catalog/2413065681 | https://findit.dtu.dk/en/catalog/20342373
ARX and ARMAX | ? | https://findit.dtu.dk/en/catalog/2438448153
Two-stage steady state identification | 1 | https://findit.dtu.dk/en/catalog/2351629037
TCO minimization | 1 | https://findit.dtu.dk/en/catalog/2389473119
Steady-state-signal identification | 1 | https://findit.dtu.dk/en/catalog/6529977 |  | Online method for calculating variance; then, with well adjusted window size, physical HVAC signals were investigated, while the thresholds for standard deviation begin tuned. Different entering and leaving levels are used. It is shown taht in case of fault (refrigerant undercharge), the method is still operating correctly.
Modelling
Heat transfer with fins | 0 | https://findit.dtu.dk/en/catalog/2286251445
Importance of liquid separators | 1 | https://findit.dtu.dk/en/catalog/2358407839
Pressure drop | 0 | https://findit.dtu.dk/en/catalog/142253916 | https://findit.dtu.dk/en/catalog/8331024
Cascade motivation | 0 | https://findit.dtu.dk/en/catalog/2265197447
Two-stage pressure optimization | 1 | https://findit.dtu.dk/en/catalog/8869259
Stability of sub and supercritical CO2 flows | 1 | https://findit.dtu.dk/en/catalog/242611474
Control, fault tolerance, adaptive control (not explicitly searched yet)
PID control | 1 | https://findit.dtu.dk/en/catalog/266555737
Model free control, no pressure sensing | 1 | https://findit.dtu.dk/en/catalog/234690685
Fault tolerant superheat control | 1 | https://findit.dtu.dk/en/catalog/2319900603
Thermoeconomic evolutionary NN control | 1 | https://findit.dtu.dk/en/catalog/2392294154
Self Tuning Adaptive Control | borrowed | https://findit.dtu.dk/en/catalog/2358760511
Distributed model based control | 1 | https://findit.dtu.dk/en/catalog/2389378809
Expectation Maximization
GMM creation, detection of anomaly with ML |  | https://findit.dtu.dk/en/catalog/2407756036 |  | EM is used for GMM to set-up a normal operation model, then a combination of particle filtering, machine learning and voting techniques are used together with correlation clustering of sensors, for anomaly detection.
Hidden Markov Model on simulated AUV platform |  | https://findit.dtu.dk/en/catalog/2349441346 |  | 2 (detection) and 6 (isolation) pieces of EM algorithm are set-up and tested for, using current and drift signals of the motors simulating an AUV unit, both application are successful.
EM-GMM with K-means algorithm for satellites |  | https://findit.dtu.dk/en/catalog/2392117782 |  | Fault detection computation optimization is done for GMM-EM models. Only one parameter is optimized in one iteration. It is shown that the CPC (coefficient performance coefficience) drops from 90% to 85% percent, but the cost time improves with three orders of magnitude.
EM-GMM with missing data |  | https://findit.dtu.dk/en/catalog/271000354 |  | Conventionally missing data are ignored; in this paper, the partial consideration of non-entire data-vectors are considered. Likelihood is maximized with discarding the missing dimensions. The method is using a closed form solution for multiple missing data pattern, in other words, the data is not expected to be missing always at the same location. The results are tested on simulation of a physical problem, missing 50% of the data, and improvement is shown with regard to the conventional methods
EM for forward-backward Kalman filter |  | https://findit.dtu.dk/en/catalog/240427997 |  | EM algorithm is used as an augmentation of the Kalman filter, detection and isolating fault profiles of an electro-hydraulic system. In the forward Kalman step, the parameters are found, in the backward steps, fault evaluation is done. The method is used to reestimate the correct behaviour in case of sensor or actuator faults, showing the occasional limitations for certain perturbation frequencies with cross-power spectral density plots.